## Sheet1
Item | Inspection/service interval | Flexibility | Flexibility where premises, or part thereof, remains open | Maintained through temporary closure
Statutory passenger carrying lifting equipment and accessories thorough examination | 6 monthly | None | Must not be used past due date | No
Statutory goods only lifting equipment thorough examination | Annual | None | Must not be used past due date | No
Lift service | Monthly | Yes | Postpone by up to 3 months. Shut defective lifts down | No
Statutory pressure systems stautory plant examination | Various | None | Must not be used past due date | No
Fall protection equipment e.g. mansafe/eyebolts test | Annual | None | Must not be used past due date | No
Fire alarm service | 3/6 monthly | Yes | Can be extended to six monthly from quarterly | Yes
Emergency lighting duration test | Annual | Yes | Can be completed in-house to ensure a minimum of 1 hour duration | No
Sprinkler service | 6 monthly | Yes | Postpone by up to 3 months if there are no defects | Yes
Refuge EVC service | 6 monthly | Yes | Postpone and restrict access to floors occupied by relevant disabled persons if outstations fail | No
Fire extinguisher service | Annual | Yes | Postpone by up to 3 months but carry out operational check when service is due | No
Kitchen extract ductwork cleaning | Various | Yes | Postpone where equipment served by the canopy is not in use | No
Fixed fire suppression system for kitchen equipment | 6 monthly | Yes | Postpone where equipment covered in not in use | No
Private fire hydrant testing | Annual | Yes | Postpone by up to 6 months | Wherever possible
Wet/dry riser | Annual | Yes | Postpone by up to 3 months | Wherever possible
Ventilation system | Annual | Yes | Postpone by up to 3 months | No
Lightning protection | Every 13 months | Yes | Postpone by up to 3 months | Yes
Laundry extract ductwork cleaning | Annual | Yes | Postpone by up to 3 months | No
Linen chute inspection | Annual | Yes | Postpone by up to 3 months. Remove from use if defective | No
Fire risk assessments review | Biennial | Yes | Postpone indefinately if in-house review is carried out | No
Fixed electrical installation inspection/test | 5 yearly | Yes | Postpone by up to 6 months if there are no outstanding code 1 or 2 defects | Yes
Fixed electrical installation inspection/test (wet leisure) | Annual | Yes | Postpone by 3 months if there are no outstanding code 1 or 2 defects | Yes
PAT testing | Annual | Yes | Postpone and implement quarterly visual checks of all equipment | No
Gas safety checks | Annual | Yes | No flexibility for equipment in use. Postpone where equipment is switched off and isolated | Yes for equipment in use
Calorifier/buffer vessel inspection | Annual | Yes | Postpone by up to 3 months | Wherever possible
Water softener service | Annual | Yes | Postpone by up to 3 months | Wherever possible
Cold water storage tank inspection | Annual | Yes | Postpone but implement monthly in-house visual checks by trained personnel | Wherever possible
Domestic water sampling | 6 monthly | Yes | Postpone where not required by the legionella risk assessment | No
Domestic hot and cold water system risk assessment | Biennial | Yes | Postpone indefinately if in-house review is carried out | No
Pool balance tank cleaing | Annual | Yes | Postpone by up to 6 months. Close if water chemistry parameters cannot be maintained | No
Spa balance tank cleaning | 6 monthly | Yes | Postpone by up to 3 months. Close if water chemistry parameters cannot be maintained | No
Pool/spa water chmemistry testing | Monthly | Yes | Postpone by 1 month. Close if water chemistry levels cannot be maintained within parameter | No
Gym equipment service | Annual | Yes | Postpone but remove from use if defective | No
Asbestos re-survey | Biennial | Yes | Postpone but carry out condition check of material in situ | No
Movable wall inspection | Annual | Yes | Postpone but remove from use if defective | No
Electronic barriers, gates, doors and shutters etc | Annual | Yes | Postpone but remove from use if defective | No